## Confined Space Inventory
Building No. | Building Name | Space Type | Location | Permit Required? | Utility to be Serviced | Shop(s) | Orientation | Number of Entry and Exit Points
2 | Administration A wing | Sump Pit | North end | Yes | Sump pump | M70
2 | Administration A wing | Sump Pit | South end |  | Sump pump | M70
3 | Administration B wing | Sump Pit | East end |  | Sump pump | M70
4 | Anthropology | Sump Pit |  |  | Sump pump | M70
127 | Architecture North | Sewerage Ejector Pit | Outside on East sidewalk |  | SEP | M70
88 | Architecture South | Sewerage Ejector Pit |  |  | SEP | M70
43 | Armstrong Hall | Sewerage Ejector Pit | Main EQ room on south end |  | SEP | M70
87 | Art | Sewerage Ejector Pit |  |  | SEP | M70
38A | Best Hall A wing | Utility Vault 5 | Intersection of Forest & Lemon in front of Student Services Building |  | Steam & chilled water | M70
38B | Best Hall B wing | Utility Vault 4 | On Forest infront of Best Hall |  | Steam & chilled water | M70
38C | Best Hall C wing | Sump Pit | C wing |  | Sump pump | M70
40 | Business Adminstration A wing | Sewerage Ejector Pit | Main EQ room |  | SEP | M70
40C | Business Adminstration C wing | Sewerage Ejector Pit |  |  | SEP | M70
72 | Cancer Research Center | Sump Pit | Older wing |  | Sump pump | M70
72 | Cancer Research Center | Sump Pit | New wing |  | Sump pump | M70
15 | Central Plant | Man hole | North side of bulding on sidewalk |  | Blowdown receptor for boiler | M70
15 | Central Plant | Sump Pit | East end of basement |  | Sump pump | M70
15 | Central Plant | Sump Pit | West end of basement |  | Sump pump | M70
55 | Classroom Office Building | Sewerage Ejector Pit | Basement |  | SEP | M70
55 | Classroom Office Building | Sewerage Ejector Pit | Basement |  | SEP | M70
55 | Classroom Office Building | Sump Pit | Basement |  | Sump pump | M70
16 | Cowden Family Resources | Sump Pit |  |  | Sump pump | M70
9 | Dixie Gammage | Crawl Space | Crawl space under building |  |  | M70
53G | Engineering Center G wing | Sump Pit |  |  | Sump pump | M70
63 | Engineering Research Center | Sump Pit |  |  | Acid sump pump | M70
63 | Engineering Research Center | Sump Pit |  |  | Sump pump | M70
85 | Goldwater Center | Sump Pit | Basement |  | Sump pump | M70
85 | Goldwater Center | Sewerage Ejector Pit | Basement |  | SEP | M70
85 | Goldwater Center | Utility Vault | Outside GWC on Northeast corner in sidewalk |  | Steam, chilled water, electric | M70
1 | Grady Gammage | Sump Pit | EQ room in tunnel |  | Sump pump | M70
1 | Grady Gammage | Sump Pit | NW corner of parking lot |  | Sump pump | M70
14 | Hayden Hall | Utility Vault 1 | NW corner of College & Apache |  | Steam & chilled water | M70
14 | Hayden Hall | Utility Vault 2 | NW corner of College & Apache |  | Steam & chilled water | M70
14 | Hayden Hall | Utility Vault 3 | NE corner of Forest & Apache |  | Steam & chilled water | M70
14 | Hayden Hall | Sump Pit |  |  | Sump pump | M70
10 | Hayden Library | Sump Pit | Under stairs |  | Sump pump | M70
10 | Hayden Library | Sewerage Ejector Pit | North equipment room |  | SEP | M70
10 | Hayden Library | Sand Trap | North equipment room |  | Sand Trap | M70
| ICA | Sewerage Ejector Pit | Basement |  | SEP | M70
| ICA | Sewerage Ejector Pit |  |  | SEP | M70
26A | Irish Hall A wing | Crawl Space | A wing |  |  | M70
12 | Language & Literature | Sewerage Ejector Pit | South side |  | SEP | M70
12 | Language & Literature | Sewerage Ejector Pit |  |  | SEP | M70
56A | Life Sciences A wing | Sewerage Ejector Pit | Room 69, main EQ room |  | SEP | M70
56B | Life Sciences B wing | Shaft | EQ room shaft |  |  | M70
56C | Life Sciences C wing | Sewerage Ejector Pit | Sub-basement |  | SEP | M70
56E | Life Sciences E wing | Sewerage Ejector Pit | Sub-sub basement |  | SEP | M70
56E | Life Sciences E wing | Sump Pit | Sub-sub basement |  | Storm water pump | M70
27 | Lyceum Theater | Sewerage Ejector Pit | Basement |  | SEP | M70
61 | Manzanita Hall | Sewerage Ejector Pit | In construction area |  | SEP | M70
61 | Manzanita Hall | Utility Vault |  |  | Steam, chilled water, electric | M70/M80
34 | Matthews Center | Sewerage Ejector Pit |  |  | SEP | M70
34 | Matthews Center | Sump Pit | EQ room |  | Sump pump | M70
34 | Matthews Center | Sump Pit | EQ room |  | Sump pump | M70
33 | Matthews Hall | Attic | Attic |  |  | M70
35 | Memorial Union | Sewerage Ejector Pit | North end by film developing center |  | SEP | M70
35 | Memorial Union | Sewerage Ejector Pit | By Credit Union |  | SEP | M70
37 | Moeur | Crawl Space |  |  |  | M70
84 | Music Additon | Sewerage Ejector Pit |  |  | SEP | M70
84 | Music Building | Sewerage Ejector Pit | Basement, below stage to East |  | SEP | M70
84 | Music Building | Sump Pit | Basement, in costume closet at bottom of stairs |  | Sump pump | M70
86 | Neeb Hall | Sump Pit | EQ room |  | Sump pump | M70
48 | Nelson Fine Arts | Sewerage Ejector Pit | Main EQ room in Fine Arts section by loading dock |  | SEP | M70
48 | Nelson Fine Arts | Sewerage Ejector Pit | In Galvin Playhouse side |  | SEP | M70
7 | Nursing | Sewerage Ejector Pit |  |  | SEP | M70
51F | Palo Verde East | Sewerage Ejector Pit | Lobby |  | SEP | M70
51G | Palo Verde West | Sump Pit |  |  | Sump pump | M70
| Parking Structure 1 | Sump Pit | North entrance |  | Sump pump | M70
6B | Payne Hall | Sewerage Ejector Pit | Basement main EQ room, SE end |  | SEP | M70
6B | Payne Lecture Hall | Sump Pit |  |  | Sump pump | M70
| Physical Education Annex | Tunnel | Dead end tunnel under annex |  |  | M70
57E | Physical Sciences E wing | Water Meter Pit | City of Tempe, north of PSE is sidewalk along University Drive |  | Water meter | M70
57E | Physical Sciences E wing | Water Meter Pit | City of Tempe, north of PSE is sidewalk along University Drive |  | Water meter | M70
13 | Psychology | Sump Pit |  |  |  | M70
| Residential Life Center Expansion | Sump Pit |  |  | Sump pump | M70
| Residential Life Center North Expansion | Utility Vault | North |  | Steam & chilled water | M70
| Residential Life Center North Expansion | Utility Vault | South |  | Steam & chilled water | M70
143 | Ross-Blakely Library | Sump Pit | SE corner |  | Sump pump | M70
143 | Ross-Blakely Library | Sump Pit | NW corner |  | Sump pump | M70
5 | Social Sciences | Water Meter Pit | City of Tempe, NW corner in mall |  | Water meter | M70
24A | Stauffer Hall | Sewerage Ejector Pit | A Wing Basement, NW EQ room |  | SEP | M70
46 | Student Recreation Complex | Sump Pit | Basement |  | Sump pump | M70
45 | Student Service Building | Sump Pit | North end of tunnel entrance |  | Sump pump | M70
11 | University Club | Crawl Space | Access through ventilation screen |  |  | M70
69 | Wells Fargo Arena | Sewerage Ejector Pit | Tunnel EQ room entrance, room 22 |  | SEP | M70
69 | Wells Fargo Arena | Sewerage Ejector Pit | Down west ramp to basketball floor |  | SEP | M70
| Bookstore | Mechanical Piping Vault | North side east corner in landscape area |  | Steam, chilled water | M70

## Pre-Entry Checklist
ARIZONA STATE UNIVERSITY
Confined Space Pre-Entry Checklist
Job Location:
Evaluator's Name: |  | Signature:
Date: |  | Time:
This checklist must be used prior to entering any confined space to determine whether a permit is required.
|  |  | Yes | No
1 | Your survey of the surrounding area shows it to be free of hazards such as drifting vapors from tanks, vehicles or motors, piping or sewers, combustible materials/debris etc.? |  | ( ) | ( )
2 | Your knowledge of the space's contents, industrial or other discharges, and mechanical or electrical systems indicate this area is likely to remain free of dangerous air contaminants and other hazards while occupied? |  | ( ) | ( )
3 | The work to be performed in the space will not create a hazardous atmosphere or condition. |  | ( ) | ( )
If you answered "No" to the statements above, you must complete the bottom portion of this checklist and obtain a permit from your supervisor before proceeding. A "Yes" response to all statements indicates that this is a "Non-Permit Required Confined Space" and you may proceed with the entry.
|  |  | Yes | No
1 | Have you been trained in the operation of the gas monitor to be used? |  | ( ) | ( )
2 | Has a gas monitor functional bump test been performed this shift on the gas monitor to be used? |  | ( ) | ( )
3 | Did you test the atmosphere of the confined space prior to entry? |  | ( ) | ( )
4 | Did the atmosphere check as acceptable (no alarms given)? |  | ( ) | ( )
5 | Will the atmosphere be continually monitored while the space is occupied? |  | ( ) | ( )
If you answered "No" to any of the statements above, DO NOT ENTER. Contact your supervisor for further instruction. If you answered "Yes" to all statements above, proceed to the "Confined Space Entry Permit".
NOTES:
Contact ASU Department of Public Safety in the event of an emergency - 911

## Permit
ARIZONA STATE UNIVERSITY
Confined Space Entry Permit
Date & Time Issued: | [5 empty] | Date & Time Expires:
Job Site: | [5 empty] | Job Site Supervisor:
Equipment to be Serviced:
Type of Work to be Performed:
1 | Atmospheric Checks:
|  | Time: |  |  | Oxygen: |  | (>19.5% or <22.0%)
|  | Explosive: |  | (LEL<10%) | Toxic: |  | (<10ppm H2S)
|  |  |  | (methane CH4) | Toxic: |  | (Carbon Monoxide [CO] ppm)
2 | Source Isolation: |  |  |  |  | N/A | Yes | No
| Pumps or lines blinded, disconnected or blocked |  |  |  |  | ( ) | ( ) | ( )
3 | Ventilation Modification:
| Mechanical |  |  |  |  | ( ) | ( ) | ( )
| Natural Ventilation Only |  |  |  |  | ( ) | ( ) | ( )
4 | Atmospheric check after isolation and ventilation:
|  | Time: |  |  | Oxygen: |  | (>19.5% or <22.0%)
|  | Explosive: |  | (LEL<10%) | Toxic: |  | (<10ppm H2S)
|  |  |  | (methane CH4) | Toxic: |  | (Carbon Monoxide [CO] ppm)
Entry Checklist:
1 | Entry, standby, and backup personnel: |  |  |  |  | N/A | Yes | No
| Successfully completed required training? |  |  |  |  | ( ) | ( ) | ( )
| Was pre-entry training conducted? |  |  |  |  | ( ) | ( ) | ( )
2 | Equipment checked:
| Direct reading gas monitor |  |  |  |  | ( ) | ( ) | ( )
| Safety harness and lifelines |  |  |  |  | ( ) | ( ) | ( )
| Hoisting equipment |  |  |  |  | ( ) | ( ) | ( )
Powered communications
| Protective clothing |  |  |  |  | ( ) | ( ) | ( )
| All electric equipment is Class I, Division 1, Group D |  |  |  |  | ( ) | ( ) | ( )
and Non-sparking tools?
3 | Rescue Procedure: |  | Contact ASU Department of Public Safety at 911 to roll Tempe Fire Department
(Cell phones call 480-965-3456)
Permit and checklist prepared by: | [5 empty] | Approved by:
(Print & Sign Name) |  |  |  |  | Project Supervisor (Print & Sign Name)
Reviewed by:
|  | Entry Personnel |  |  |  | Entry Personnel
This permit will be posted at the job site. Return job site copy to Risk Management following job completion.

## Hazard Overview
ARIZONA STATE UNIVERSITY
Confined Space Overview and Hazard Identification
Permit Required Confined | Potential Hazards
Spaces | Oxygen Deficiency | Mechanical | Biological | Suffocation | Hydrogen Sulfide Gas | Explosive Atmosphere | Chlorine Gas | Products of Work Activities
Sewer Manholes | X |  | X | X | X | X |  | X
Swimming Pool Tanks at Mona Plumber | X | X |  | X | X |  | X | X
Sump Pits | X |  | X |  | X | X |  | X
Air Handlers |  | X | [5 empty] | X
Water Tanks under the Soccer Field | X |  |  | X |  |  |  | X
Boiler Tanks | X |  |  | X |  |  |  | X
Tunnels - normally non-permit required, certain areas may contain: | (as a result of work activities) | [6 empty] | X
Precautions | Oxygen monitoring/ventilation |  |  |  |  | Continuous explosive gas monitoring

## Signage
DANGER
Permit Required Confined Space
No Entry
Please contact your supervisor prior to entry
to obtain the required permit.

## Detailed Hazard
ATMOSPHERIC HAZARDS | EXPLANATORY NOTES | METHOD OF TEST | EFFECTS OF HAZARD | EXAMPLES
Explosive Atmosphere | Before entering confined space, tests for presence of an explosive atmosphere must be done. It should be noted that air-borne dust from grain, fine ground metals or other materials can form an explosive atmosphere. Explosive gases may displace oxygen. Note: Oxygen enrichment or deficiency can cause error in combustible gas detector readings. | Combustible gas detector - explosive gases must be monitored by equipment that can detect the lower explosives limit (L.E.L.) and upper explosive limit (U.E.L.). Residues may have to be disturbed to allow for release of explosive gases. | Explosion/burns/multiple injuries/death | 1. Methane (or natural gas) CH4 - sources - gas line leaks, decaying matter. May be found adjacent to land fill sites; backed up, sluggish sewers.
2. Gasoline and other solvents - Storage tanks and adjacent areas, sewer systems proximity to pipelines, accidental spills may have definite odor.
Oxygen Deficiency | Deficiency - Acceptable breathing air contains between 19.5%-21.4% oxygen Air containing less than acceptable amounts of oxygen is a hazardous atmosphere. | Oxygen detection monitor. | Could result in slowing down of pulse rate, disorientation, unconsciousness, death. | Oxygen (02) deficiency can be caused by displacement by other gases, or by biological or chemical reactions (rusting, burning).
Oxygen Enrichment | Enrichment - An atmosphere that contain more than the acceptable amount of oxygen (21.4%). Oxygen enrichment can cause an error in explosive meter readings | Oxygen detection meter. | Creates explosive atmosphere, increases rate of chemical reaction. | Enrichment may be caused by improper blanking of oxygen lines, leaking fuelgas, welding equipment, ventilation with oxygen instead of air.
Note: Some equipment incapable of detecting for oxygen enrichment.
Toxic Gases & Vapors | Testing with appropriate detection equipment shall be undertaken to determine the presence of toxic gas(es) to create and maintain a safe environment. | Monitors - specific testors must be used for specific toxic gases, e.g.. H2S monitoring. It may be necessary to disturb residue/sludge to allow for release of toxic gases/vapors. | Can cause euphoria / disorienting effect, drowsiness, headaches, weakness, injury, disability, death. | 1. Carbon Monoxide (CO) - colorless, odorless, tasteless and very poisonous. Commonest source - internal combustion engines and decomposition of organic matter.
2. Carbon Dioxide (CO2) - Odorless. It is a heavy gas that can concentrate at lowest levels. It displaces oxygen and does not diffuse or mix readily with air.
3. Nitrogen Dioxide (NO2) - A pungent acrid odor. Product of gasoline and diesel engines.
4. Hydrogen Sulphide (H2S) - deadly gas commonly found in sewers, manure pits. Produced by decomposition of organic matter. Has a typical rotten egg odor, but higher amounts can kill the sense of smell.
Fumes, Dusts, Mists, & Fogs | These hazards are usually recognized visually | Monitors - Testers specific for each fume, dust, mist, fog must be used. | Explosion, disability, injury, burns, irritation, death poisoning | 1. Fumes - From asphalt, welding, acid fumes from washing process
2. Dust - Grain dust, sand, blasting (silica)
3. Mist - Spray application
ATMOSPHERIC HAZARDS | EXPLANATORY NOTES | METHOD OF TEST | EFFECTS OF HAZARD | EXAMPLES
Smoke | Smoke is a combination of gases, vapors, fumes and dusts | Visual - Use appropriate detection (monitoring) equipment to determine presence of toxic agent(s) | All effects of gases, dusts, vapors, mists, fumes | Result of combustion, e.g.. burning materials, smoke from welding
Biological Agents | Biological agents are found in a variety of locations. Extreme care should be taken when working near health care facilities or industrial processes using biological agents. Conscientious personal hygiene is essential. | Testing for presence of biological agents is very difficult. If type of agent(s) is known, then specific testing may be done. | Ill health, disease, disorders, irritation, death. | 1. Bacteria and viral infection.
SAFETY HAZARDS | EXPLANATORY NOTES | METHOD OF TEST | EFFECTS OF HAZARD | EXAMPLES
Entry/Exit (Access/Egress) | Openings that are small, narrow or otherwise difficult to negotiate can be a serious hazard. Where self-contained breathing apparatus is being used, openings must be of a size to allow worker with equipment properly worn to pass through. Access openings less than 700 mm (28") are not recommended. | Visual identification of obstructions that could interfere with normal movement or emergency rescue. | Injury, disability, death | 1. Exits at height that could cause falls.
2. Constricted openings
3. Angled openings
4. Exits into traffic and machinery
5. Exits at deep depths.
Ventilation Systems | Lack of adequate ventilation may cause a build-up of contaminants etc. Ventilation systems can introduce hazards into the work area, e.g. carbon monoxide (CO) fumes. | Monitoring (anemometer, smoke tubes for air movement). Toxic monitors may also be necessary to ensure good quality air. | Explosion, disease, irritation, injury, disability, death | Improper ventilation can result in:
1. Oxygen levels variation
2. Build up of toxic gases, vapors, dusts, mists, fumes (smoke).
3. Introduction of biologic agents, toxic gases, explosive gases.
Machinery/Mechanical Equipment | Make sure equipment is immobilized (de-energized) so that it will not be a hazard to workers | Visual and function testing | Injury, disability, death | Drive belts, augers, paddles, scrapers, agitators and pumps
Piping/Distribution Systems | Contents of pipes and supply lines if allowed to enter a confined space can create a life threatening situation for workers. | Monitoring, visual | Chemical poisoning, drowning, burns, injury, disability, death | Steamlines, liquid distribution lines, feed mills and cement plants
Residual Chemicals/Materials | 1. Corrosive and/or toxic chemicals remaining in a confined space. Special attention should be made to ensure that lines, valves and meters are totally drained and properly decontaminated | Monitoring | Injury, disability, death, explosion | Storage tanks, digesters, liquid distribution systems, augers.
| 2. Material that may be adhered to surfaces/walls of enclosures may collapse. | Visual, Monitoring | Engulfment, suffocation, drowning, injury, disability, death | 1. Silos, grain hoppers, fertilizer storage.
SAFETY HAZARDS | EXPLANATORY NOTES | METHOD OF TEST | EFFECTS OF HAZARD | EXAMPLES
Residual Chemicals/Materials | 3. Loose granular material that may engulf worker. | Monitoring | Injury, disability, death, explosion | 2. Sand, grains (e.g.. Flax)
| 4. Material that may encapsulate/trap other toxic/explosive materials. | Visual, Monitoring | Engulfment, suffocation, drowning, injury, disability, death | 3. a) Rust build up in fuel storafe tank
| 5. Flooding by liquids |  |  | b) sludge prevents release of Hydrogen sulphide (H2S)
4. Flooding in underground facilities
Electrical | Sources of unguarded electrical equipment - extreme caution must be taken when using conductive material around electrical surfaces (e.g.. metal ladders, lifelines, steel bars, etc.) | Only by qualified personnel | Shock, burns, injury, disability, death | 1. Underground electrical vaults and electrical distribution systems.
2. Motor control centers.
Poor Visibility | Caused by poor lighting obstructions, work process and procedure, fog/mist due to high humidity. | Visual | Injury, disability, death | Improper/inadequate lighting, poor design of confined space, work process.
Physical Obstacles | This would include obstacles that impede movement and performance of work and rescue procedures. | Visual | Inability to remove injured worker, contusions, abrasions, fractures, disability, injury, death. | Cross bracing, baffle plates, piping.
Walking / Working Surfaces | Surfaces may be irregular in shape, sloped, angled, elevated, slippery, obstructed, etc., all of which are slip and fall hazards. Work areas may require toe boards to prevent objects from falling on workers below. | Visual | Injury, disability, death | 1. Lift stations, aqueducts, dams
2. Work areas that require toe boards to prevent objects from falling on workers below.
Temperature Extremes | Temperature extremes, hot or cold, have definite health and safety hazards, as well as having a limiting effect on the ability of a worker to adequately perform tasks. | Thermometer, Heat Stress - Wet Bulb Globe Thermometer (WBGT) | 1. Cold - Frost bite, loss of coordination, hypothermia, disability, death. | 1. Working in freezers, extreme cold climate conditions.
|  |  | 2. Heat - heat exhaustion, heat stress, disorientation, death. | 2. Working in boilers, super-heated areas (cooling towers), areas that have steam / heat distribution pipes running through work areas.
Humidity | High humidity can aggravate several conditions: | Hygrometer | Can cause slips, falls, physical discomfort, heat exhaustion, affect performance of tasks. | 1. Boiler rooms
| 1. Visibility |  |  | 2. Digesters
| 2. Can cause all types of surfaces to become slippery. |  |  | 3. Freezers
3. Accelerate Heat loss.
4. Increase chill effect.
SAFETY HAZARDS | EXPLANATORY NOTES | METHOD OF TEST | EFFECTS OF HAZARD | EXAMPLES
Noise | If sound levels exceed 80 DBA then work practices shall conform to requirements of current regulations respecting Hearing Conservation and Noise Control in Workplaces. | Sound level meters | Distraction, stress, disorientation, communication problems, hearing loss. | Sources include operating equipment, such as jack hammers, pumps, grinders, other work procedures.
Vibration | Whole body vibration is a "general stressor" affecting multiple body parts / organs. | Vibration meter | White finger disease, disorientation, vertigo, circulation and nervous system disorders. | 1. Jack hammers, impact hammers / drills, shakers.
Radiation | 1. Non-ionizing | 1. Non-ionizing - specific light meters | 1. Non-ionizing topical burns. | 1. Ultra-violet and infra-red light sources.
radiation - ultra violet light, infra red light - components or sunlight.
| 2. Ionizing radiation | 2. Ionizing - Geiger counters, passive dosimeters | Ionizing - Deep body burns, radiation sickness, sterility, death | 1. X-ray equipment
| Radio-active materials (uranium) |  |  | 2. Level or density gauges in manufacturing processes.
Types: Alpha, Beta, Gamma
Hazardous Animals | Rats, pigeons, and other vermin and their by-products (excrement). | Visual | Disease, injury | Rats, pigeons, bats
Hot Work | Type of work being undertaken can create additional hazards. These hazards created by the work process will have to be considered and planned for to ensure the safety and health of workers in the confined space. | Monitoring, visual, pre-job planning, work permit system. | Injury, disability, death. | Welding
Hot Work: Where heat used or generated by work process may cause an explosion.
Cold Work | Cold Work: Situation where toxic substances or other hazards may exist. | Monitoring, visual, pre-job planning, work permit system. | Injury, disability, death. | Using solvents
Spray painting
Sand blasting
Grinding
Bonding Operations
HUMAN FACTORS | EXPLANATORY NOTES | METHOD OF TEST | EFFECTS OF HAZARD | EXAMPLES
Phobias | Some workers are not suitable for work in confined spaces. As a result of these factors they can cause injuries to themselves or others. | Medical interview screening | Injury, disability, death | 1. Claustrophobia
2. Fear of heights
Mental & Physical Condition | All workers must be mentally and physically capable of performing the work. | Visual, medical examination (pre-employment, annuals) | Injury, disability, death | 1. Intoxication (alcohol, drug abuse)
2. Impairment (prescription medication)

## Training Verification
| Name | Title | Department/Shop | Date | Time | Location
1 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
2 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
3 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
4 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
5 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
6 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
7 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
8 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
9 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
10 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
11 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
12 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
13 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
14 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
15 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
16 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
17 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
18 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
19 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
20 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
21 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
22 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
23 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
24 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
25 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
26 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
27 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
28 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
29 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
30 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
31 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
32 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
33 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
34 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
35 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
36 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
37 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
38 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
39 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
40 |  |  |  | 2001-03-14 | 8-10 AM | FM Training Center
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90