## Sheet1
Building Number | SO | Building Name | Area (sq ft) | Number of Floors | Number Below Grade | Year Built | Facility Construction/Characteristics | Facility Usage/Capabilities | Occupied | Contaminated | Type | Level | Related Documents | Comments
TRA-603 (MTR) |  | MTR Reactor Building | 45184 | 2 | 1 | 1952 | The reactor vessel is mostly on the main floor of TRA-603. It has been defuled but containes 93.5 Tons of Graphite as well as Be reflectors. The reactor vessel is above one end of the canal which is in the basement. The canal has been defueled, drained, and debris has been removed. | The reactor has been shut down and defueled. | Yes | Yes | bg | Significantly contaminted cubicles and piping systems in basement. Levels uncertain. | HAD-207, ASA-136, ASA-112 | This building is currently in use by the INL. The contactor shall coordinate with the INL contractor on demolition and utility removal plans.
TRA-604 (MTR) |  | MTR Building - Wing A (Laboratory) | 41744 | 2 | 1 | 1952 | Masonry exterior walls. Contains laboratories, radiography caves, offices, radiochemistry equipment, etc. Basement contains electrical transmission equipment (switch gear, etc.) | The building is a chemistry and radiochemistry laboratory building. It houses a number of laboratories and equipment for analytical of chemicals and radioactive elements. | Yes | Yes | bg | Potentially contaminated piping and labortory systems | ASA-112, HAD-166 | This building is currently in use by the INL. The contactor shall coordinate with the INL contractor on demolition and utility removal plans. Potentially contains piping systems that are part of VCO Appendix B, 5.8.d.
TRA-610 (MTR) |  | MTR Fan House | 3216 | 1 | 0 | 1952 | Masonry exterior walls. Located next to the MTR main stack, the building houses fans for MTR ventilation exhaust. | The building has recently been used for storage of materials and equipment by facility electricians. | No | Yes | bg | Internal blower contamination likely |  | This building in currently is use by the INL. The contactor shall coordinate with the INL contractor on demolition and utility removal plans. Conservative source term estimate in late 2001 for TRA-610 and -710 is -- C0-60 = 2.76E-3 Ci; Ba-133 = 2.46E-4 Ci; Ag-108m = 2.48E-4 Ci; Sr-90 = 6.67E-4; C-14 = 1.09E-3 Ci; Ni-63 = 2-09E-3; Eu-152 = 5.17E-4; Cs-137 = 2.48E-2 Ci.
TRA-611 (MTR) |  | Plug Storage Building | 100 | 1 | 0 | 1952 | Reinforced concrete. The plug holes consist of several pipes which extend through the wall into an earthen berm on the outside of the building. The plug holes are empty. | Out of service | No | Yes | bg | Some plug hole contamination anticipated. Labeled as contatmintion area. |  | This building is currently in use by the INL. The contactor shall coordinate with the INL contractor on demolition and utility removal plans.
TRA-624 | NE | Sewage Treatment Building | 111 | 1 | 0 | 1952 | Masonry Exterior Walls. Consists of Imhoff tank, trickling filter, and sludge pit. | Out of service. | No | Possible |  | Minor possible |  | Slight radiological contamination possible, particularly in sludge.
TRA-626 (MTR) |  | Maintenance Storage Building | 14272 | 2 | 0 | 1952 | One-room shed. Masonry exterior walls | This shed has been used to store equipment for grounds maintenance, lawn mowers, etc. | No | No |  |  |  | This building is currently in use by the INL. The contactor shall coordinate with the INL contractor on demolition and utility removal plans.
TRA-630 (MTR) |  | Catch Tank Pump House | 396 | 1 | 0 | 1996 | One-room steel frame building housing pumps and valve equipment for the TRA-730 hot waste catch tanks. | Building in use until catch RCRA closure complete under VCO. | No | Yes |  | Piping systems are contaminated. |  | This building is currently in use as part of the 730-catch tanks RCRA closure under the VCO. The contactor shall coordinate with the INL contractor on demolition and utility removal plans.
TRA-635 (MTR) |  | Material Receiving and Lab Area | 22046 | 2 | 0 | 1952 | Masonry exterior walls. High bay building. Contains out-of-service 15-ton bridge crane. | The building has recently been used for general storage and receipt of materials that are shipped into the TRA facility. It houses a recycling center and temporary waste accumulation area. It also houses a radiography cave. | Yes | Probable |  | Contamination anticipated in below-grade waste piping systems. | ASA-112 | This building is currently in use by the INL. The contactor shall coordinate with the INL contractor on demolition and utility removal plans. Potentially contains piping systems that are part of VCO Appendix B, 5.8.d.
TRA-637 (MTR) |  | Bunkhouse trailer | 600 | 1 | 0 | 1978 | Sheet metal bunk trailer. | Out of service | No | No |  |  |  | This building may have already been removed during FY 04.
TRA-642 | EM | Engineering Test Reactor Bldg. | 47762 | 3 | 2 | 1957 | Reinforced concrete with sheet metal cover. Contains considerable lead shielding. Reactor vessel contains Be blocks with no known disposition path due to transuranic content. | Reactor is defueled and vessel and canal are drained of water. The main reactor floor is used for equipment storage. An internally contaminated hot liquid waste semi tanker trailer is currently housed on the main floor, but the trailer should be removed prior to contract inception. | No | Yes | bg | Significantly contaminted cubicles in basement. Levels uncertain. 50,000- 150,000 dpm/100cm2 | ASA-105, HAD-200 and EDF TRA-2000-004. | Cubicles are still posted as contamination areas. Lead shielding in place (VCO NEW-TRA-01). Utilities include wet pipe fire suppression sprinkler system, electrical, instrument air, liquid rad waste, sewer. See VCO SITE-TANK-005 - several systems.
TRA-643 | EM | ETR Compressor Building | 11151 | 1 | 0 | 1957 | Steel framed with large open floor. Contains most of the orginal compressor equipment for ETR as it was originally configured. | Out of service. Since it was shut down, available floor space has been used for storage. Houses the equipment that was used to supply large quantities of heated, hydrocarbon-free compressed air to various experiments and other reactor support systems. | No | Yes | bg | Significantly contaminted cubicles in basement. Levels uncertain. 10,000-100,000 dpm/100cm2 | ASA-105, HAD-200 and EDF TRA-2000-004. | Contamination area is located on a mezzanine, and inside a contaminated hood. Wet pipe fire suppression sprinkler system is active. Original compressor systems largely still in place. See VCO SITE-TANK-005, several tank systems.
TRA-644 | EM | ETR Heat Exchanger Bldg | 6793 | 2 | 1 | 1957 | Masonry Exterior Walls | Out of service. The primary function of the heat exchanger building main room was to house the 12 primary coolant-to-secondary coolant heat exchangers and associated piping for ETR. The building is a high radiation area. | No | Yes | Beta-Gamma | 2000-50,000 dpm/100cm2 | ASA-105, HAD-200 and EDF TRA-2000-004. | Some areas within this building have not been surveyed to due confined space and fall protection issues. See VCO SITE-TANK-005 system TRA-012 and TRA-022.
TRA-647 | NE | ETR Office Building | 11793 | 3? | 1? | 1957 | Masonry Exterior Walls. Two floors of office space. | Out of service. Personnel are no longer housed in this building. | No | No
TRA-648 | NE | ETR Electrical Building | 9785 | 1 | 0 | 1957 | Masonry Exterior Walls. Single open floor. A diesel room in the southwest corner of the building houses one of two Superior diesel generators that supported ETR. The other Superior diesel generator is in building TRA-663 directly to the south and connected to TRA-648. | Contains banks of electrical switch gear for the ETR reactor. Some power has continued to be routed through this gear to support TRA operations even though the ETR reactor has been out of service for several years. The switch gear will be taken out of service during FY 2004. | No | No |  |  |  | See VCO SITE-TANK-005 system TRA-034.
TRA-651 (MTR) |  | Maintenance Storage Building | 672 | 1 | 0 | 1960 | Steel framed, one-room shed. | Has been used for storage of ATR fuel boxes. | No | No
TRA-654 (MTR) |  | General lab/High Bay (old ETRC) | 2400 | 2 | 0 | 1959 | Masonry exterior walls. High bay area. Contains 10-ton capacity bridge crane. | Since decontamination in the late 90s, the building has been used for physics experiments. | No | Minor, if any |  |  | ASA-112
TRA-655 | EM | ETR Air Intake Bldg. | 300 | 1 | 0 | 1957 | Reinforced Concrete. One room vented structure covering the air intake for ETR. | Out of service. | No | Yes | Beta-Gamma | Possible minimal contamination |  | There are no survey data available. Only slight contaminaion is likely.
TRA-656 | NE | Maintenance Storage Bldg | 850 | 1 | 0 | 1959 | Steel Framed, one-room shed. | This shed has been used to store general maintenance equipment. | No | No
TRA-657 (MTR) |  | MTR Plug Storage Building | 5000 | 1 | 0 | 1952 | Masonry exterior walls, single open room. The 21 plug storage holes are empty. The plug holes extend 29 feet into a 12-foot high compacted earthen berm. | The building is now used for material and equipment storage and houses a temporary waste accumulation area. | No | Yes | bg | Some contamination inside plug holes anticipated. Labeled as contamination area | ASA-112 | Plug holes were defueled, but they were not decontaminated. Therefore, they are still labeled as a contamination area.
TRA-661 (MTR) |  | Radiochemistry Laboratories | 7760 | 1 | 0 | 1962 | Masonry exterior walls. Laboratories throughout. | The building houses radiochemistry laboratories and is still in use. | Yes | Yes |  | Contaminated laboratory and piping systems probable | ASA-112 | This building is currently in use by the INL. The contactor shall coordinate with the INL contractor on demolition and utility removal plans. Potentially contains piping systems that are part of VCO Appendix B, 5.8.d.
TRA-663 | NE | Superior Diesel Building | 1120 | 1 | 0 | 0 | Masonry Exterior Walls. One-room building to house one of two Superior diesel genrators that supported ETR. The other Superior diesel generator is housed in the southwest corner of TRA-648 directly to the north. | Contains out-of-service Superior diesel generator | No | No |  |  |  | See VCO SITE-TANK-005 system TRA-034.
TRA-664 | EM | Hot Storage Building | 800 | 1 | 0 | 1961 | Steel Framed. One-room shed. No utilities. | This shed was used in the past for housing contaminated equipment. All equipment has been removed, but residual contamination remains. | No | Yes | Beta-Gamma | 1000-5000 dpm/100cm2 |  | Small soil contamination area and possible areas of low level fixed contamination
TRA-665 (MTR) |  | Storage Building | 776 | 1 | 0 | 1962 | This single room reinforced concrete building is attached to the MTR building. | It is used to store radioactive sources and material. | No | Minor potential |  | Minimal potential contamination | ASA-112
TRA-668 (MTR) |  | MTR North Wing Extension | 3596 | 1 | 0 | 1956 | Masonary exterior walls. Laboratories throughout. | Physics laboratoires. Currently in use. |  |  |  | Contaminated laboratory and piping systems probable | ASA-112 | This building is currently in use by the INL. The contactor shall coordinate with the INL contractor on demolition and utility removal plans. Potentially contains piping systems that are part of VCO Appendix B, 5.8.d.
TRA-690 (MTR) |  | Storage Building | 80 | 1 | 0 | 1993 | Prefabricated modular equipment storage shed. Houses hydraulic unit and power supply for technology development project in TRA-603. | Equipment storage | No | No |  |  | ASA-112
TRA-704 |  | ETR Primary Filter Pit |  |  |  |  | Concrete vault. Hatch covers require a crane to lift them. | Underground pit houses two filters surrounded with four inches of lead and encased with carbon steel and high density concrete. |  | Yes | Beta-Gamma | Cobalt-60 - 8.4 Ci; Barium-137m - 159.6 Ci; Cesium-137 - 168 Ci; Strontium-90 - 1.29 Ci | ASA-105, HAD-200 and EDF TRA-2000-004. | Located in hatched pit to the north of TRA-647. VCO SITE-TANK-005 tank system TRA-033. Tank Database 98TRA00357.
TRA-705 |  | ETR Secondary Filter Pit |  |  |  |  | Concrete vault housing canister charcoal filters. Hatch covers require a crane to lift them. | Houses two filters, is the same size as the primary pit. |  | Yes | Beta-Gamma | Cobalt-60 - 8.4 Ci; Barium-137m - 159.6 Ci; Cesium-137 - 168 Ci; Strontium-90 - 1.29 Ci | ASA-105, HAD-200 and EDF TRA-2000-004. | VCO SITE-TANK-005 tank system TRA-033. Tank Database 98TRA00233. Underground pit houses two filters surrounded with four inches of lead and encased with carbon steel and high density concrete.
TRA-706 |  | Delay tanks |  |  |  |  | There are two cylindrical delay tanks in this pit. The major diameters of the housings are approximately 17 ft and 14 ft. The housings and concrete ends are about 70 ft long. The tops of the tanks are about 8 ft below grade. | These tanks originally provided ETR exhaust delay to allow time for short-lived nuclides to decay before being vented through the stack. |  | Yes | Beta-Gamma | Unknown | ASA-105, HAD-200 and EDF TRA-2000-004. | VCO SITE-TANK-005 tank system TRA-033. Tank Database 98TRA00231. No measurable external contamination. Internals assumed to be contaminated.
TRA-709 (MTR) |  | MTR Air Intake (MTR |  |  |  |  | Air intake for TRA-603 and -604. 8' X 8' free-standing metal structure. Louvered, screened intakes on all but west side. |  |  | No
TRA-710 (MTR) |  | MTR Exhaust Stack (MTR) |  |  |  | 1952 | Concrete, free-standing stack, 250 feet tall, 10 feet in damater at base. | Vents ventilation exhaust from the MTR reactor complex through TRA-610 the MTR fan house. It's main current use is to vent the MTR reactor vessel and laboratories (TRA-604) |  | Yes |  | Some contamination probable inside stack |  | Conservative source term estimate in late 2001 for TRA-610 and -710 is -- C0-60 = 2.76E-3 Ci; Ba-133 = 2.46E-4 Ci; Ag-108m = 2.48E-4 Ci; Sr-90 = 6.67E-4; C-14 = 1.09E-3 Ci; Ni-63 = 2-09E-3; Eu-152 = 5.17E-4; Cs-137 = 2.48E-2 Ci. This structure is currently in use by the INL. The contactor shall coordinate with the INL contractor on demolition and utility removal plans.
TRA-732 |  | Sewage Treatment Plant |  |  |  |  | Old out-of-service sewage plant. Consists of Imhoff tank, trickling filter, and sludge pit. Minor rad contamination is possible, particularly the sludge. |  |  | Yes | Beta-Gamma | Minor |  | Out of service. Consists of Imhoff tank, trickling filter and sludge pit. Connected to Blg. TRA-624. Slight rad. contamination likely.
TRA-752 |  | ETR Transformer pad |  |  |  |  | 15,000 KVA tranformers. At contract inception only one of the eaight transformers will be active and will be serviceing the ETR complex. |  |  | No | None
TRA-753 |  | ETR exhaust stack |  |  |  |  | Concrete. This was the main ETR stack. It is currently used only to exhaust ETR building complex ventilation. 250 feet high, 14 feet in diameter at base and 6 feet in diameter at top. |  |  | Possible |  |  |  | Mastic lining contains PCBs.
TRA-755 |  | ETR Filter Pit |  |  |  |  | Pumice block construction. | Houses fans that were associated with experimenter's service exhaust. Exhausted waste gasses from ETR to main stack. |  | Yes | Beta-Gamma | Cobalt-60 - 6.9 Ci; Barium-137m - 131.9 Ci; Cesium-137 - 138 Ci; Strontium-90 - 1.06 Ci | ASA-105, HAD-200 and EDF TRA-2000-004. | VCO SITE-TANK-005 tank system TRA-033. Tank Database 98TRA00285, 98TRA00286, 98TRA00287. Underground filter pit housings containing the three loop filters enclosed in steel canisters surrounded by high density concrete.
TRA-779 |  | CERCLA Storage Unit | approx. 100 |  |  |  | This small prefabricated storage unit is on what was formerly a concrete decontamination pad. | It is used to store purge water from monitor well sampling at TRA until analytical data are obtained and a disposotion path for the purge water can be verified. Electricity is supplied to the unit, but no other utilitities. |  | No |  |  |  | The contractor is free to approach the INL contractor to take over control of this structure rather than demolish and remove it when the ICP contractor no longer has need for it.
TRA-784 (MTR) |  | Liquid Nitrogen Tank |  |  |  | 2000 | 3,000 gal. Contains liquid nitrogen for laboratory - vertical, cylindrical tank. Tank is plumbed into the northeast corner of TRA-657 where laboratory personnel retrieve liquid nitrogen rom the tank. |  |  | No |  |  |  | The INL has the prerogative to remove the tank for its use at an alternate location prior to its removal by the ICP contractor. If it has not been removed by the time the ICP contractor is ready to demolish the MTR complex then removing the tank remains the responsibility of the ICP contractor.
Note on N23: John Martin: