## FA.6
Lighting Survey Form
Project Name: | [14 empty] | Sponsor Name:
Please fill out one copy of this form for each customer site involved in the project where lighting measures are being installed.
Fill in all non-shaded cells of the lighting equipment survey completely. Shaded values are automatically calculated or taken from the Standard Wattage Table. If additional lines are needed to complete the survey, insert lines into the table before the last shaded line. Use the tables below to determine stipulated operating hours and power adjustment factors, where appropriate. Note that annual kW and kWh savings do not include any interactive savings. The interactive demand and energy savings are listed.
| Operating Hours and Coincidence Factor Table |  |  |  |  | Power Adjustment Factors Table | [5 empty] | Interactive Demand and Energy Savings
| (for use with Stipulated Hours Method or when coincidence factor will not be measured) |  |  |  |  | (**for use with Stipulated Controls Savings Method) | [5 empty] | (Interactive savings should be added to all stipulated building types except Parking Stucture)
| Building Type |  | Hours | Coincidence Factor |  | Control Measure Type (DC = Daylight Controls) |  |  |  | Power Adjustment Factor (PAF) |  | Building Type |  |  |  |  | Interactive HVAC Demand Savings | Interactive HVAC Energy Savings
| Stipulated Office |  | 3760 | 0.8 |  | No controls measures |  |  |  | 1 |  | Stipulated Office |  |  |  |  | 10% | 5%
| Stipulated Non-24-Hour Supermarket/Retail/Restaurant |  | 4250 | 0.95 |  | Stipulated DC - continuous dimming |  |  |  | 0.7 |  | Stipulated Non-24-Hour Supermarket/Retail/Restaurant |  |  |  |  | 10% | 5%
| Stipulated Education (K-12; no summer session) |  | 2150 | 0.82 |  | Stipulated DC - multiple step dimming |  |  |  | 0.8 |  | Stipulated Education (K-12; no summer session) |  |  |  |  | 10% | 5%
| Stipulated 24-Hour Supermarket/Retail |  | 6900 | 0.95 |  | Stipulated DC - ON/OFF |  |  |  | 0.9 |  | Stipulated 24-Hour Supermarket/Retail |  |  |  |  | 10% | 5%
| Stipulated In-Patient Health Care |  | 3750 | 0.6 |  | Stipulated Occupancy Sensor (OS) |  |  |  | 0.7 |  | Stipulated In-Patient Health Care |  |  |  |  | 10% | 5%
| Higher Education (College / University) |  | 2085 | 0.67 |  | Stipulated OS w/DC - Continuous Dimming |  |  |  | 0.6 |  | Higher Education (College / University) |  |  |  |  | 10% | 5%
| Multi-Family Housing, Common Areas |  | 4772 | 0.85 |  | Stipulated OS w/DC - Multiple Step Dimming |  |  |  | 0.65 |  | Multi-Family Housing, Common Areas |  |  |  |  | 10% | 5%
| Parking Structure |  | 7884 | 1 |  | Stipulated OS w/DC - ON/OFF |  |  |  | 0.65 |  | Parking Structure |  |  |  |  | 0% | 0%
Space Description |  |  |  |  | Pre-Retrofit Equipment | [7 empty] | Post-Retrofit Equipment | [7 empty] | Annual kW Savings | Annual kWh Savings
Line Item | Floor | Room/Area Description | Usage Area Type | Coincidence Factor | Fixture Code | # of Fixtures | # of Non-op Fixtures* | kW per Fixture | kW per Space | kWh per Space | Pre Control Device | Pre Operating Hours | Fixture Code | # of Fixtures | kW per Fixture | kW per Space | kWh per Space | Post Control Device | Power Adjustment Factor** | Post Operating Hours
1 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
2 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
3 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
4 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
5 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
6 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
7 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
8 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
9 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
10 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
11 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
12 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
13 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
14 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
15 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
16 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
17 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
18 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
19 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
20 | [7 empty] | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
Insert additional lines above this line.
[6 empty] | 0 | 0 |  | 0 | 0 |  |  |  | 0 |  | 0 |  |  |  |  | 0 | 0
* If the number of non-operating fixtures is greater than 10%, the savings calculation shall be reduced accordingly.

## Wattage Lookup
FIXTURE CODE | LAMP CODE | WATT/ FIXT
CF11/1-SCRW | CFC11W | 11
CF13/1-SCRW | CFC13W | 13
CF15/1-SCRW | CFC15W | 15
CF15/2-SCRW | CFC15W | 30
CF15/3-SCRW | CFC15W | 45
CF15/4-SCRW | CFC15W | 60
CF16/1-SCRW | CFC16W | 16
CF17/1-SCRW | CFC17W | 17
CF18/1-SCRW | CFC18W | 18
CF18/1-L-SCRW | CFS18W | 18
CF20/1-SCRW | CFC20W | 20
CF20/2-SCRW | CFC20W | 40
CF23/1-SCRW | CFC23W | 23
CF23/1-L-SCRW | CFS23W | 23
CF23/2-SCRW | CFC23W | 46
CF25/1-SCRW | CFC25W | 25
CF28/1-SCRW | CFC28W | 28
CF26/1-L-SCRW | CFS26W | 26
CF44/1-L-SCRW | CFQ44W | 44
CF7/1-SCRW | CFC7W | 7
CF9/1-SCRW | CFC9W | 9
CFD9/1-LOCK | CFD9W | 12
CFD13/1-LOCK | CFD13W | 15
CFD10/1 | CFD10W | 16
CFD16/1 | CFD16W | 26
CFD21/1 | CFD21W | 26
CFD28/1 | CFD28W | 35
CFD38/1 | CFD38W | 46
CFM13/1-L | CFM13W | 16
CFM13/2-L | CFM13W | 30
CFM18/1-L | CFM18W | 20
CFM18/2-L | CFM18W | 40
CFM26/1-L | CFM26W | 29
CFM26/2-L | CFM26W | 51
CFM32/1-L | CFM32W | 35
CFM42/1-L | CFM42W | 48
CFM42/8-L | CFM42W | 314
CFQ10/1 | CFQ10W | 15
CFQ13/1 | CFQ13W | 17
CFQ13/1-L | CFQ13W | 15
CFQ13/2 | CFQ13W | 31
CFQ13/2-L | CFQ13W | 28
CFQ13/3 | CFQ13W | 48
CFQ15/1 | CFQ15W | 20
CFQ17/1 | CFQ17W | 24
CFQ17/2 | CFQ17W | 48
CFQ18/1 | CFQ18W | 26
CFQ18/1-L | CFQ18W | 20
CFQ18/2 | CFQ18W | 45
CFQ18/2-L | CFQ18W | 38
CFQ18/4 | CFQ18W | 90
CFQ20/1 | CFQ20W | 23
CFQ20/2 | CFQ20W | 46
CFQ22/1 | CFQ22W | 24
CFQ22/2 | CFQ22W | 48
CFQ22/3 | CFQ22W | 72
CFQ23/1 | CFQ23W | 27
CFQ25/1 | CFQ25W | 33
CFQ25/2 | CFQ25W | 66
CFQ26/1 | CFQ26W | 33
CFQ26/1-L | CFQ26W | 27
CFQ26/2 | CFQ26W | 66
CFQ26/2-L | CFQ26W | 50
CFQ26/3 | CFQ26W | 99
CFQ26/6-L | CFQ26W | 150
CFQ28/1 | CFQ28W | 33
CFQ28/1-L | CFQ28W | 31
CFQ28/2-L | CFQ28W | 60
CFQ42/8-L | CFQ42W | 305
CFQ9/1 | CFQ9W | 14
CFQ9/2 | CFQ9W | 23
CFT13/1 | CFT13W | 17
CFT13/1-L | CFT13W | 15
CFT13/2 | CFT13W | 31
CFT13/2-L | CFT13W | 28
CFT13/3 | CFT13W | 48
CFT18/1 | CFT18W | 24
CFT18/1-L | CFT18W | 20
CFT18/2 | CFT18W | 38
CFT22/1 | CFT22W | 27
CFT22/2 | CFT22W | 54
CFT22/4 | CFT22W | 108
CFT24/1 | CFT24W | 32
CFT26/1 | CFT26W | 32
CFT26/1-L | CFT26W | 27
CFT26/2-L | CFT26W | 51
CFT28/1 | CFT28W | 33
CFT28/2 | CFT28W | 66
CFT32/1-L | CFM32W | 34
CFT32/2-L | CFM32W | 62
CFT32/6-L | CFM32W | 186
CFT36/1 | CFT36W | 51
CFT40/1 | CFT40W | 46
CFT40/1-L | CFT40W | 43
CFT40/2 | CFT40W | 85
CFT40/2-L | CFT40W | 72
CFT40/3 | CFT40W | 133
CFT40/3-L | CFT40W | 105
CFT5/1 | CFT5W | 9
CFT5/1-LOCK | CFT5W | 8
CFT5/2 | CFT5W | 18
CFT55/1-L | CFT55W | 60
CFT55/2-L | CFT55W | 110
CFT55/3-L | CFT55W | 170
CFT55/4-L | CFT55W | 220
CFT7/1 | CFT7W | 10
CFT7/2 | CFT7W | 21
CFT9/1 | CFT9W | 12
CFT9/2 | CFT9W | 23
CFT9/3 | CFT9W | 34
ECF5/1 | CFT5W | 9
ECF5/2 | CFT5W | 20
ECF6/1 | CFT6W | 13
ECF6/2 | CFT6W | 26
ECF7/1 | CFT7W | 10
ECF7/2 | CFT7W | 21
ECF9/1 | CFT9W | 12
ECF9/2 | CFT9W | 20
EF2/2 | F2T1 | 5
EF6/1 | F6T5 | 9
EF6/2 | F6T5 | 18
EF8/1 | F8T5 | 12
EF8/2 | F8T5 | 24
EI10/2 | I10 | 20
EI15/1 | I15 | 15
EI15/2 | I15 | 30
EI20/1 | I20 | 20
EI20/2 | I20 | 40
EI25/1 | I25 | 25
EI25/2 | I25 | 50
EI34/1 | I34 | 34
EI34/2 | I34 | 68
EI40/1 | I40 | 40
EI40/2 | I40 | 80
EI5/1 | I5 | 5
EI5/2 | I5 | 10
EI50/2 | I50 | 100
EI6/1 | 6S6 | 6
EI6/2 | 6S6 | 12
EI7.5/1 | I7.5 | 8
EI7.5/2 | I7.5 | 15
ELED2/1 | LED2W | 6
ELED2/2 | LED2W | 9
ELED3 | LED3W | 3
F1.51LS | F15T8 | 19
F1.51SS | F15T12 | 19
F1.52LS | F15T8 | 36
F1.52SS | F15T12 | 36
F21HS | F24T12/HO | 62
F21ILL | F17T8 | 20
F21ILL/T2 | F17T8 | 17
F21ILL/T2-R | F17T8 | 15
F21ILL/T3 | F17T8 | 16
F21ILL/T3-R | F17T8 | 14
F21ILL/T4 | F17T8 | 15
F21ILL/T4-R | F17T8 | 14
F21ILL-R | F17T8 | 17
F21ILU | F17T8 | 17
F21ILU-R | F17T8 | 15
F21LL | F17T8 | 16
F21LL/T2 | F17T8 | 16
F21LL/T3 | F17T8 | 17
F21LL/T4 | F17T8 | 17
F21LL-R | F17T8 | 15
F21PL-H | F14T5 | 18
F21PHL-H | F24T5HO | 27
F21SL | F17T8 | 24
F21SS | F20T12 | 25
F22HS | F24T12/HO | 90
F22ILL | F17T8 | 33
F22ILL/T4 | F17T8 | 31
F22ILL/T4-R | F17T8 | 28
F22ILL-R | F17T8 | 29
F22ILU | F17T8 | 31
F22ILU-R | F17T8 | 29
F22LL | F17T8 | 31
F22LL/T4 | F17T8 | 34
F22LL-R | F17T8 | 28
F22PL-H | F14T5 | 33
F22PHL-H | F24T5HO | 52
F22PS | F13T5 | 26
F22SS | F20T12 | 50
F23ILL | F17T8 | 47
F23ILL-H | F17T8 | 49
F23ILL-R | F17T8 | 43
F23ILU | F17T8 | 45
F23ILU-R | F17T8 | 40
F23LL | F17T8 | 52
F23LL-R | F17T8 | 41
F23PL/2-H | F14T5 | 51
F23PHL/2-H | F24T5HO | 80
F23SS | F20T12 | 62
F24ILL | F17T8 | 61
F24ILL-R | F17T8 | 55
F24ILU | F17T8 | 59
F24ILU-R | F17T8 | 51
F24LL | F17T8 | 68
F24LL-R | F17T8 | 57
F24PL/2-H | F14T5 | 67
F24PHL/2-H | F24T5HO | 105
F24PS | F13T5 | 53
F24SS | F20T12 | 100
F26SS | F20T12 | 146
F31EE/T2 | F30T12/ES | 33
F31EL | F30T12/ES | 26
F31ES | F30T12/ES | 42
F31ES/T2 | F30T12/ES | 33
F31ILL | F25T8 | 26
F31ILL/T2 | F25T8 | 23
F31ILL/T2-H | F25T8 | 24
F31ILL/T2-R | F25T8 | 23
F31ILL/T3 | F25T8 | 22
F31ILL/T3-R | F25T8 | 22
F31ILL/T4 | F25T8 | 22
F31ILL/T4-R | F25T8 | 22
F31ILL-H | F25T8 | 28
F31ILL-R | F25T8 | 27
F31ILU | F25T8 | 22
F31ILU-R | F25T8 | 20
F31ILU/T2 | F25T8 | 22
F31ILU/T2-R | F25T8 | 20
F31ILU/T3-R | F25T8 | 19
F31ILU/T4-R | F25T8 | 19
F31LL | F25T8 | 24
F31LL/T2 | F25T8 | 23
F31LL/T3 | F25T8 | 24
F31LL/T4 | F25T8 | 22
F31LL-H | F25T8 | 26
F31LL-R | F25T8 | 23
F31PL-H | F21T5 | 25
F31PHL-H | F39T5HO | 44
F31SE/T2 | F30T12 | 37
F31SHS | F36T12/HO | 70
F31SL | F30T12 | 31
F31SS | F30T12 | 46
F31SS/T2 | F30T12 | 41
F32EE | F30T12/ES | 66
F32EL | F30T12/ES | 50
F32EL/T4 | F25T12 | 50
F32ES | F30T12/ES | 73
F32ILL | F25T8 | 46
F32ILU | F25T8 | 44
F32ILU-R | F25T8 | 40
F32ILU/T4-R | F25T8 | 39
F32ILL/T4 | F25T8 | 44
F32ILL/T4-R | F25T8 | 43
F32ILL-H | F25T8 | 48
F32ILL-R | F25T8 | 46
F32ILL/2-R | F25T8 | 54
F32LL | F25T8 | 46
F32LL/T4 | F25T8 | 45
F32LL-H | F25T8 | 50
F32LL-R | F25T8 | 42
F32LL-V | F25T8 | 70
F32PL-H | F21T5 | 48
F32PHL-H | F39T5HO | 86
F32SE | F30T12 | 74
F32SHS | F36T12/HO | 114
F32SL | F30T12 | 58
F32SS | F30T12 | 75
F33ES | F30T12/ES | 115
F33ILL | F25T8 | 67
F33ILL-R | F25T8 | 66
F33ILU | F25T8 | 64
F33ILU-R | F25T8 | 57
F33LL | F25T8 | 72
F33LL-R | F25T8 | 62
F33PL/2-H | F21T5 | 73
F33PHL/2-H | F39T5HO | 130
F33SE | F30T12 | 120
F33SS | F30T12 | 127
F34EE | F30T12/ES | 132
F34ILL | F25T8 | 87
F34ILL-R | F25T8 | 86
F34ILL/2-R | F25T8 | 92
F34ILU | F25T8 | 85
F34ILU-R | F25T8 | 78
F34LL | F25T8 | 89
F34LL-R | F25T8 | 84
F34PL/2-H | F21T5 | 96
F34PHL/2-H | F39T5HO | 172
F34SE | F30T12 | 148
F34SL | F30T12 | 116
F34SS | F30T12 | 150
F36EE | F30T12/ES | 198
F36ES | F30T12/ES | 219
F36ILL | F25T8 | 134
F36ILL-R | F25T8 | 134
F36SE | F30T12 | 213
F36SS | F30T12 | 225
F40SE/D1 | None | 4
F40SE/D2 | None | 8
F41EE | F40T12/ES | 43
F41EE/D2 | F40T12/ES | 43
F41EE/T2 | F40T12/ES | 36
F41EHS | F48T12/HO/ES | 80
F41EIS | F48T12/ES | 51
F41EL | F40T12/ES | 32
F41IELL | F32T8/WM | 29
F41IELL-H | F32T8/WM | 39
F41IELL-R | F32T8/WM | 27
F41IELL/T2 | F32T8/WM | 27
F41IELL/T3 | F32T8/WM | 26
F41IELL/T4 | F32T8/WM | 26
F41ES | F40T12/ES | 48
F41IAL | F25T12 | 25
F41IAL/T2-R | F25T18 | 19
F41IAL/T3-R | F25T17 | 20
F41IAL/T4-R | F25T17 | 20
F41ILL | F32T8 | 31
F41ILL/T2 | F32T8 | 30
F41ILL/T2-H | F32T8 | 33
F41ILL/T2-R | F32T8 | 26
F41ILL/T3 | F32T8 | 30
F41ILL/T3-H | F32T8 | 31
F41ILL/T3-R | F32T8 | 26
F41ILL/T4 | F32T8 | 28
F41ILL/T4-R | F32T8 | 26
F41ILL-H | F32T8 | 41
F41ILL-R | F32T8 | 29
F41ILL-VR | F32T8 | 25
F41IELL-VR | F32T8/WM | 24
F41IELU | F32T8/WM | 28
F41IELU-H | F32T8/WM | 32
F41IELU/T2-R | F32T8/WM | 23
F41IELU/T2 | F32T8/WM | 26
F41IELU/T3-R | F32T8/WM | 22
F41IELU/T3 | F32T8/WM | 25
F41IELU/T4-R | F32T8/WM | 22
F41IELU/T4 | F32T8/WM | 25
F41ILU | F32T8 | 29
F41ILU-H | F32T8 | 34
F41ILU-R | F32T8 | 25
F41ILU/T2 | F32T8 | 28
F41ILU/T2-R | F32T8 | 24
F41ILU/T3 | F32T8 | 27
F41ILU/T3-R | F32T8 | 24
F41ILU/T4 | F32T8 | 27
F41ILU/T4-R | F32T8 | 24
F41LE | F32T8 | 35
F41LL | F32T8 | 32
F41LL-VR | F32T8 | 28
F41LL/T2 | F32T8 | 30
F41LL/T2-H | F32T8 | 35
F41LL/T2-R | F32T8 | 27
F41LL/T3 | F32T8 | 31
F41LL/T3-H | F32T8 | 33
F41LL/T3-R | F32T8 | 25
F41LL/T4 | F32T8 | 30
F41LL/T4-R | F32T8 | 26
F41LL-H | F32T8 | 39
F41LL-R | F32T8 | 27
F41PL-H | F28T5 | 33
F41PL/T2-H | F28T5 | 32
F41PHL-H | F54T5HO | 62
F41PHL/T2-H | F54T5HO | 59
F41IRLL | F32T8-28W | 27
F41IRLL/D1-R | F32T8-28W | 27
F41IRLL-VR | F32T8-28W | 22
F41IRLU | F32T8-28W | 25
F41IRLU-R | F32T8-28W | 22
F41SE | F40T12 | 43
F41SE/T2 | F40T12 | 36
F41SHS | F48T12/HO | 85
F41SIL | F40T12 | 46
F41SIL/T2 | F40T12 | 37
F41SIS | F40T12 | 60
F41SIS/T2 | F40T12 | 52
F41SS | F40T12 | 43
F41SS/T2 | F40T12 | 43
F41SVS | F48T12/VHO | 140
F41TS | F40T10 | 51
F42EE | F40T12/ES | 72
F42EE/2 | F40T12/ES | 86
F42EE/D2 | F40T12/ES | 76
F42EHS | F42T12/HO/ES | 135
F42EIS | F48T12/ES | 82
F42EL | F40T12/ES | 60
F42IELL | F32T8/WM | 54
F42IELL-H | F32T8/WM | 72
F42IELL-R | F32T8/WM | 48
F42ES | F40T12/ES | 72
F42IAL/T4-R | F25T12 | 40
F42IAL-R | F25T12 | 39
F42ILL | F32T8 | 59
F42ILL/2 | F32T8 | 62
F42ILL/T4 | F32T8 | 56
F42ILL/T4-R | F32T8 | 51
F42ILL-H | F32T8 | 77
F42ILL-R | F32T8 | 52
F42ILL/2-R | F32T8 | 62
F42ILL-V | F32T8 | 79
F42IELU | F32T8/WM | 52
F42IELU-R | F32T8/WM | 45
F42IELL/T4 | F32T8/WM | 52
F42IELL/T4-R | F32T8/WM | 46
F42IELU/T4-R | F32T8/WM | 44
F42IELU/T4 | F32T8/WM | 51
F42ILU | F32T8 | 55
F42ILU-R | F32T8 | 48
F42ILU/T4 | F32T8 | 54
F42ILU/T4-R | F32T8 | 48
F42IRLL | F32T8-28W | 49
F42IRLL-VR | F32T8-28W | 42
F42IRLU | F32T8-28W | 48
F42IRLU-R | F32T8-28W | 44
F42IRLU-V | F32T8-28W | 65
F42LE | F32T8 | 71
F42LL | F32T8 | 60
F42LL-VR | F32T8 | 49
F42LL/2 | F32T8 | 64
F42LL/T4 | F32T8 | 59
F42LL/T4-R | F32T8 | 53
F42LL-H | F32T8 | 70
F42LL-R | F32T8 | 54
F42LL-V | F32T8 | 85
F42PL-H | F28T5 | 63
F42PHL-H | F54T5HO | 117
F42SE | F40T12 | 72
F42SE/D2 | F40T12 | 76
F42SHS | F48T12/HO | 145
F42SIL | F40T12 | 74
F42SIS | F40T12 | 103
F42SS | F40T12 | 72
F42SVS | F48T12/VHO | 252
F43EE | F40T12/ES | 115
F43EE/T2 | F40T12/ES | 108
F43EHS | F42T12/HO/ES | 215
F43EIS | F48T12/ES | 133
F43EL | F40T12/ES | 92
F43ELL-R | F32T8/WM | 70
F43ES | F40T12/ES | 115
F43ES/T2 | F40T12/ES | 108
F43IAL-R | F25T12 | 60
F43ILL | F32T8 | 87
F43IELL | F32T8/WM | 79
F43IELL-R | F32T8/WM | 70
F43IELL-H | F32T8/WM | 105
F43IELL-VR | F32T8/WM | 66
F43IELL/2 | F32T8/WM | 83
F43IELL/2-R | F32T8/WM | 78
F43IELL/2-H | F32T8/WM | 111
F43ILL/2 | F32T8 | 90
F43ILL/2-R | F32T8 | 83
F43ILL/2-H | F32T | 118
F43ILL/T2-R | F32T8 | 83
F43ILL-H | F32T8 | 111
F43ILL-R | F32T8 | 78
F43ILL-V | F32T8 | 113
F43IELU | F32T8/WM | 76
F43IELU-R | F32T8/WM | 66
F43ILU | F32T8 | 82
F43ILU-R | F32T8 | 73
F43IRLL | F32T8-28W | 72
F43IRLL/D1 | F32T8-28W | 79
F43IRLL-VR | F32T8-28W | 63
F43IRLU | F32T8-28W | 71
F43IRLU-R | F32T8-28W | 65
F43IRLU-V | F32T8-28W | 96
F43LE | F32T8 | 110
F43LL | F32T8 | 93
F43LL-VR | F32T8 | 72
F43LL/2 | F32T8 | 92
F43LL-H | F32T8 | 98
F43LL-R | F32T8 | 76
F43PL/2-H | F28T5 | 96
F43PHL/2-H | F54T5HO | 179
F43SE | F40T12 | 115
F43SHS | F48T12/HO | 230
F43SIL | F40T12 | 120
F43SS | F40T12 | 115
F43SVS | F48T12/VHO | 377
F44EE | F40T12/ES | 144
F44EE/D3 | F40T12/ES | 148
F44EE/D4 | F40T12/ES | 152
F44EHS | F48T12/HO/ES | 270
F44EIS | F48T12/ES | 164
F44EL | F40T12/ES | 120
F44ES | F40T12/ES | 144
F44EVS | F48T12/VHO/ES | 420
F44IAL-R | F25T12 | 80
F44ILL | F32T8 | 112
F44ILL/2 | F32T8 | 118
F44ILL/2-R | F32T8 | 104
F44ILL/2-H | F32T8 | 154
F44ILL/2-V | F32T8 | 158
F44ILL-R | F32T8 | 102
F44ILL-V | F32T8 | 151
F44IELL | F32T8/WM | 104
F44IELL-R | F32T8/WM | 91
F44IELU | F32T8/WM | 101
F44IELU-R | F32T8/WM | 88
F44IELL/2 | F32T8/WM | 108
F44IELL/2-R | F32T8/WM | 96
F44IELL/2-H | F32T8/WM | 144
F44ILU | F32T8 | 108
F44ILU-R | F32T8 | 95
F44IRLL | F32T8-28W | 98
F44IRLL-R | F32T8-28W | 85
F44IRLL-VR | F32T8-28W | 81
F44IRLU | F32T8-28W | 96
F44IRLU-V | F32T8-28W | 131
F44LE | F32T8 | 142
F44LL | F32T8 | 118
F44LL-VR | F32T8 | 94
F44LL/2 | F32T8 | 120
F44LL-R | F32T8 | 105
F44PL/2-H | F28T5 | 126
F44PHL/2-H | F54T5HO | 234
F44SE | F40T12 | 144
F44SHS | F48T12/HO | 290
F44SIL | F40T12 | 148
F44SS | F40T12 | 144
F44SVS | F48T12/VHO | 484
F45ILL | F32T8 | 148
F46EE | F40T12/ES | 216
F46EL | F40T12/ES | 186
F46ES | F40T12/ES | 216
F46ILL/2 | F32T8 | 174
F46ILL/2-R | F32T8 | 156
F46ILL-R | F32T8 | 156
F46ILL/2-V | F32T8 | 226
F46IELU/2 | F32T8/WM | 152
F46IELU/2-R | F32T8/WM | 132
F46ILU/2 | F32T8 | 164
F46ILU/2-R | F32T8 | 146
F46LL | F32T8 | 182
F46PHL/3-H | F54T5HO | 351
F46SE | F40T12 | 216
F46SL | F40T12 | 186
F46SS | F40T12 | 216
F48EE | F40T12/ES | 288
F48ES | F40T12/ES | 288
F48ILL | F32T8 | 224
F48ILL/2-R | F32T8 | 204
F48ILL-R | F32T8 | 204
F48SE | F40T12 | 288
F48SS | F40T12 | 288
F51ILL | F40T8 | 36
F51ILL/T2 | F40T8 | 36
F51ILL/T3 | F40T8 | 35
F51ILL/T4 | F40T8 | 34
F51ILL-R | F40T8 | 43
F51PL-H | F35T5 | 40
F51PHL-H | F80T5HO | 90
F51SHE | F60T12/HO | 88
F51SHL | F60T12/HO | 69
F51SHS | F60T12/HO | 92
F51SL | F60T12 | 44
F51SS | F60T12 | 63
F51SVS | F60T12/VHO | 165
F52ILL | F40T8 | 72
F52ILL/T4 | F40T8 | 67
F52ILL-H | F40T8 | 80
F52ILL-R | F40T8 | 73
F52PL-H | F35T5 | 78
F52PHL/2-H | F80T5HO | 179
F52SHE | F60T12/HO | 176
F52SHL | F60T12/HO | 138
F52SHS | F60T12/HO | 168
F52SL | F60T12 | 88
F52SS | F60T12 | 128
F52SVS | F60T12/VHO | 310
F53ILL | F40T8 | 106
F53ILL-H | F40T8 | 108
F53PL/2-H | F35T5 | 119
F54ILL | F40T8 | 134
F54ILL-H | F40T8 | 126
F54PL/2-H | F35T5 | 157
F61ISL | F72T12 | 68
F61SHS | F72T12/HO | 106
F61SS | F72T12 | 76
F61SVS | F72T12/VHO | 180
F62ISL | F72T12 | 108
F62SE | F72T12 | 122
F62SHE | F72T12/HO | 194
F62SHL | F72T12/HO | 167
F62SHS | F72T12/HO | 200
F62SL | F72T12 | 108
F62SS | F72T12 | 142
F62SVS | F72T12/VHO | 330
F63ISL | F72T12 | 176
F63SS | F72T12 | 202
F64ISL | F72T12 | 216
F64SE | F72T12 | 244
F64SHE | F72T12/HO | 388
F64SS | F72T12 | 244
F81EE | F96T12/ES | 75
F81EE/T2 | F96T12/ES | 62
F81EHL | F96T12/HO/ES | 80
F81EHS | F96T12/HO/ES | 113
F81EL | F96T12/ES | 69
F81EL/T2 | F96T12/ES | 55
F81ES | F96T12/ES | 75
F81ES/T2 | F96T12/ES | 62
F81EVS | F96T12/VHO/ES | 205
F81IELU | F96T8/WM | 51
F81ILL | F96T8 | 58
F81ILL/T2 | F96T8 | 55
F81ILL/T2-R | F96T8 | 49
F81ILL-H | F96T8 | 68
F81ILL-R | F96T8 | 57
F81ILL-V | F96T8 | 71
F81LHL/T2 | F96T8/HO | 80
F81ILU | F96T8 | 53
F81SE | F96T12 | 75
F81SE/T2 | F96T12 | 62
F81SGS | F96T17 | 235
F81SHS | F96T12/HO | 121
F81SL | F96T12 | 69
F81SL/T2 | F96T12 | 55
F81SS | F96T12 | 75
F81SS/T2 | F96T12 | 62
F81SVS | F96T12/VHO | 205
F82EE | F96T12/ES | 123
F82EHE | F96T12/HO/ES | 207
F82EHL | F96T12/HO/ES | 173
F82EHS | F96T12/HO/ES | 207
F82EL | F96T12/ES | 110
F82ES | F96T12/ES | 123
F82EVS | F96T12/VHO/ES | 390
F82IELU | T8F96/WM | 100
F82ILL | F96T8 | 109
F82ILL-R | F96T8 | 98
F82ILL-V | F96T8 | 149
F82ILU | F96T8 | 105
F82LHL | F96T8/HO | 160
F82SE | F96T12 | 123
F82SHE | F96T12/HO | 207
F82SHL | F96T12/HO | 173
F82SHS | F96T12/HO | 207
F82SL | F96T12 | 110
F82SS | F96T12 | 123
F82SVS | F96T12/VHO | 380
F83EE | F96T12/ES | 198
F83EHE | F96T12/HO/ES | 319
F83EHS | F96T12/HO/ES | 319
F83EL | F96T12/ES | 179
F83ES | F96T12/ES | 198
F83EVS | F96T12/VHO/ES | 585
F83ILL | F96T8 | 167
F83SE | F96T12 | 198
F83SHE | F96T12/HO | 319
F83SHS | F96T12/HO | 319
F83SL | F96T12 | 179
F83SVS | F96T12/VHO | 585
F84EE | F96T12/ES | 246
F84EHE | F96T12/HO/ES | 414
F84EHL | F96T12/HO/ES | 346
F84EHS | F96T12/HO/ES | 414
F84EL | F96T12/ES | 220
F84ES | F96T12/ES | 246
F84EVS | F96T12/VHO/ES | 760
F84ILL | F96T8 | 219
F84ILL-V | F96T8 | 298
F84LHL | F96T8/HO | 320
F84SE | F96T12 | 246
F84SHE | F96T12/HO | 414
F84SHL | F96T12/HO | 346
F84SHS | F96T12/HO | 414
F84SL | F96T12 | 220
F84SVS | F96T12/VHO | 760
F86EE | F96T12/ES | 369
F86EHS | F96T12/HO/ES | 519
F86ILL | F96T8 | 328
F86SE | F96T12 | 328
F86SS | F96T12 | 328
F88EHE | F96T12/HO/ES | 828
F88SHS | F96T12/HO | 828
FC12/1 | FC12T9 | 31
FC12/2 | FC12T9 | 62
FC16/1 | FC16T9 | 35
FC20 | FC6T9 | 20
FC22 | FC8T9 | 20
FC32 | FC12T9 | 40
FC40 | FC16T9 | 42
FC6/1 | FC6T9 | 25
FC8/1 | FC8T9 | 26
FC8/2 | FC8T9 | 52
FU1EE | FU40T12/ES | 43
FU1ES | FU40T12/ES | 43
FU1ILL | FU31T8/6 | 31
FU1LL | FU31T8/6 | 32
FU1LL-R | FU31T8/6 | 27
FU1ILU | FU32T8/6 | 29
FU1ILU-H | FU32T8/6 | 34
FU1SE | FU40T12 | 43
FU1SS | FU40T12 | 43
FU2EE | FU40T12/ES | 72
FU2EL | FU40T12/ES | 63
FU2ES | FU40T12/ES | 72
FU2ILL | FU31T8/6 | 59
FU2ILL/T4 | FU31T8/6 | 56
FU2ILL/T4-R | FU31T8/6 | 51
FU2ILL-H | FU31T8/6 | 65
FU2ILL-R | FU31T8/6 | 52
FU2ILU | FU32T8/6 | 55
FU2ILU-R | FU32T8/6 | 48
FU2LL | FU31T8/6 | 60
FU2LL/T2 | FU31T8/6 | 59
FU2LL-R | FU31T8/6 | 54
FU2SE | FU40T12 | 72
FU2SL | FU40T12 | 63
FU2SS | FU40T12 | 72
FU3EE | FU40T12/ES | 115
FU3ILL | FU31T8/6 | 89
FU3ILL-R | FU31T8/6 | 78
FU3ILU-R | FU32T8/6 | 73
FU3ILU | FU32T8/6 | 81
FU3SE | FU40T12 | 115
H100/1 | H100 | 100
H150/1 | H150 | 150
H150/2 | H150 | 300
H250/1 | H250 | 250
H300/1 | H300 | 300
H35/1 | H35 | 35
H42/1 | H42 | 42
H45/1 | H45 | 45
H45/2 | H45 | 90
H50/1 | H50 | 50
H50/2 | H50 | 100
H500/1 | H500 | 500
H52/1 | H52 | 52
H55/1 | H55 | 55
H55/2 | H55 | 110
H60/1 | H60 | 60
H72/1 | H72 | 72
H75/1 | H75 | 75
H75/2 | H75 | 150
H90/1 | H90 | 90
H90/2 | H90 | 180
HLV50/1 | H50/LV | 60
HPS100/1 | HPS100 | 138
HPS1000/1 | HPS1000 | 1100
HPS150/1 | HPS150 | 188
HPS200/1 | HPS200 | 250
HPS250/1 | HPS250 | 295
HPS310/1 | HPS310 | 365
HPS35/1 | HPS35 | 46
HPS360/1 | HPS360 | 414
HPS400/1 | HPS400 | 465
HPS50/1 | HPS50 | 66
HPS70/1 | HPS70 | 95
I100/1 | I100 | 100
I100/2 | I100 | 200
I100/3 | I100 | 300
I100/4 | I100 | 400
I100/5 | I100 | 500
I1000/1 | I1000 | 1000
I100E/1 | I100/ES | 90
I100EL/1 | I100/ES/LL | 90
I110/1 | I110 | 110
I116/1 | I116 | 116
I120/1 | I120 | 120
I120/1 | I120 | 120
I120/2 | I120 | 240
I125/1 | I125 | 125
I130/1 | I130 | 130
I135/1 | I135 | 135
I135/2 | I135 | 270
I15/1 | I15 | 15
I15/2 | I15 | 30
I150/1 | I150 | 150
I150/2 | I150 | 300
I150/3 | I150 | 450
I1500/1 | I1500 | 1500
I150E/1 | I150/ES | 135
I150EL/1 | I150/ES/LL | 135
I160/1 | I160 | 160
I170/1 | I170 | 170
I20/1 | I20 | 20
I20/2 | I20 | 40
I200/1 | I200 | 200
I200/2 | I200 | 400
I2000/1 | I2000 | 2000
I200L/1 | I200/LL | 200
I25/1 | I25 | 25
I25/2 | I25 | 50
I25/4 | I25 | 100
I25/6 | I25 | 150
I250/1 | I250 | 250
I30/1 | I30 | 30
I300/1 | I300 | 300
I300/4 | I300 | 1200
I34/1 | I34 | 34
I34/2 | I34 | 68
I36/1 | I36 | 36
I40/1 | I40 | 40
I40/2 | I40 | 80
I400/1 | I400 | 400
I40E/1 | I40/ES | 34
I40EL/1 | I40/ES/LL | 34
I42/1 | I42 | 42
I448/1 | I448 | 448
I45/1 | I45 | 45
I50/1 | I50 | 50
I50/2 | I50 | 100
I500/1 | I500 | 500
I52/1 | I52 | 52
I52/2 | I52 | 104
I54/1 | I54 | 54
I54/2 | I54 | 108
I55/1 | I55 | 55
I55/2 | I55 | 110
I60/1 | I60 | 60
I60/2 | I60 | 120
I60/3 | I60 | 180
I60/4 | I60 | 240
I60/5 | I60 | 300
I60E/1 | I60/ES | 52
I60EL/1 | I60/ES/LL | 52
I60EL/2 | I60/ES/LL | 104
I65/1 | I65 | 65
I65/1 | I65 | 65
I65/2 | I65 | 130
I67/1 | I67 | 67
I67/2 | I67 | 134
I67/3 | I67 | 201
I69/1 | I69 | 69
I7.5/1 | I7.5 | 8
I7.5/2 | I7.5 | 15
I72/1 | I72 | 72
I75/1 | I75 | 75
I75/2 | I75 | 150
I75/3 | I75 | 225
I75/4 | I75 | 300
I750/1 | I750 | 750
I75E/1 | I75/ES | 67
I75EL/1 | I75/ES/LL | 67
I80/1 | I80 | 80
I85/1 | I85 | 85
I90/1 | I90 | 90
I90/2 | I90 | 180
I90/3 | I90 | 270
I93/1 | I93 | 93
I95/1 | I95 | 95
I95/2 | I95 | 190
LED12GA | LED 12" Green Arrow | 8
LED12GB | LED 12" Green Ball | 12
LED12RA | LED 12" Red Arrow | 7
LED12RB | LED 12" Red Ball | 10
LED12YA | LED 12" Yellow Arrow | 9
LED12YB | LED 12" Yellow Ball | 17
LED8GB | LED 8" Green Ball | 8
LED8RB | LED 8" Red Ball | 6
LED8YB | LED 8" Yellow Ball | 12
LEDPH16OO | Overlay Outline Hand | 8
LEDPH16OF | Overlay Filled Hand | 9
LEDPP16OO | Overlay Outline Person | 8
LEDPP16OF | Overlay Filled Person | 8
LEDPH12OO | Overlay Outline Hand | 6
LEDPH12OF | Overlay Filled Hand | 8
LEDPP12OO | Overlay Outline Person | 6
LEDPP12OF | Overlay Filled Person | 7
LEDPH16SO | Side by Side Outline Hand | 6
LEDPH16SF | Side by Side Filled Hand | 11
LEDPP16SO | Side by Side Outline Person | 7
LEDPP16SF | Side by Side Filled Person | 8
LEDPCOUNT | Countdown Led | 7
LEDPH12SF | Side by Side Filled Hand | 7
LEDPP12SO | Side by Side Outline Person | 4
NEONMPH | Neon | 45
NEONMPP | Neon | 38
NEONMPDW | Neon | 81
NEONEPP | Neon | 26
NEONEPH | Neon | 26
MH100/1 | MH100 | 128
MH1000/1 | MH1000 | 1080
MH125/1-PS | MH125 | 150
MH150/1 | MH150 | 190
MH1500/1 | MH1500 | 1610
MH175/1 | MH175 | 215
MH200/1 | MH200 | 232
MH250/1 | MH250 | 295
MH32/1 | MH32 | 43
MH320/1 | MH320 | 357
MH350/1 | MH350 | 380
MH360/1 | MH360 | 418
MH400/1 | MH400 | 458
MH400/2 | MH400 | 916
MH450/1 | MH450 | 485
MH50/1 | MH50 | 72
MH70/1 | MH70 | 95
MH750/1 | MH750 | 850
MV100/1 | MV100 | 125
MV1000/1 | MV1000 | 1075
MV160/1 | MV160-SB | 160
MV175/1 | MV175 | 205
MV250/1 | MV250 | 290
MV40/1 | MV40 | 50
MV400/1 | MV400 | 455
MV400/2 | MV400 | 910
MV50/1 | MV50 | 74
MV700/1 | MV700 | 780
MV75/1 | MV75 | 93
Removed | None | 0