## dosag2
Streeter-Phelps analysis of critical dissolved oxygen sag.
Based on Lotus File DOSAG2.WK1 Revised 19-Oct-93
INPUT
1. EFFLUENT CHARACTERISTICS
Discharge (cfs): |  |  | 1.86
CBOD5 (mg/L): |  |  | 40
NBOD (mg/L): |  |  | 2.6
Dissolved Oxygen (mg/L): |  |  | 2
Temperature (deg C): |  |  | 20.7
2. RECEIVING WATER CHARACTERISTICS
Upstream Discharge (cfs): |  |  | 16
Upstream CBOD5 (mg/L): |  |  | 1.5
Upstream NBOD (mg/L): |  |  | 0.2
Upstream Dissolved Oxygen (mg/L): |  |  | 8.32
Upstream Temperature (deg C): |  |  | 20.7
Elevation (ft NGVD): |  |  | 1540
Downstream Average Channel Slope (ft/ft): |  |  | 0.00088
Downstream Average Channel Depth (ft): |  |  | 0.46
Downstream Average Channel Velocity (fps): |  |  | 0.98
3. REAERATION RATE (Base e) AT 20 deg C (day^-1): |  |  | 3.57
Reference | Applic. | Applic. | Suggested
| Vel (fps) | Dep (ft) | Values
Churchill | 1.5 - 6 | 2 - 50 | 41.7025
O'Connor and Dobbins | .1 - 1.5 | 2 - 50 | 41.1227
Owens | .1 - 6 | 1 - 2 | 89.6341
Tsivoglou-Wallace | .1 - 6 | .1 - 2 | 3.5737
4. BOD DECAY RATE (Base e) AT 20 deg C (day^-1): |  |  | 2.51
Reference |  |  | Suggested
Value
Wright and McDonnell, 1979 |  |  | 2.5085
OUTPUT
1. INITIAL MIXED RIVER CONDITION
CBOD5 (mg/L): |  |  | 5.5095
NBOD (mg/L): |  |  | 0.44994
Dissolved Oxygen (mg/L): |  |  | 7.6618
Temperature (deg C): |  |  | 20.7
2. TEMPERATURE ADJUSTED RATE CONSTANTS (Base e)
Reaeration (day^-1): |  |  | 3.6298
BOD Decay (day^-1): |  |  | 2.592
3. CALCULATED INITIAL ULTIMATE CBODU AND TOTAL BODU
Initial Mixed CBODU (mg/L): |  |  | 8.1022
Initial Mixed Total BODU (CBODU + NBOD, mg/L): |  |  | 8.5522
4. INITIAL DISSOLVED OXYGEN DEFICIT
Saturation Dissolved Oxygen (mg/L): |  |  | 8.477
Initial Deficit (mg/L): |  |  | 0.81514
5. TRAVEL TIME TO CRITICAL DO CONCENTRATION (days): |  |  | 0.28699
6. DISTANCE TO CRITICAL DO CONCENTRATION (miles): |  |  | 4.6023
7. CRITICAL DO DEFICIT (mg/L): |  |  | 2.9025
8. CRITICAL DO CONCENTRATION (mg/L): |  |  | 5.5745

## idod2
Dissolved oxygen concentration following initial dilution.
References: EPA/600/6-85/002b and EPA/430/9-82-011
Based on Lotus File IDOD2.WK1 Revised 19-Oct-93
INPUT
1. Dilution Factor at Mixing Zone Boundary: | 10
2. Ambient Dissolved Oxygen Concentration (mg/L): | 6.5
3. Effluent Dissolved Oxygen Concentration (mg/L): | 4
4. Effluent Immediate Dissolved Oxygen Demand (mg/L): | 0
OUTPUT
Dissolved Oxygen at Mixing Zone Boundary (mg/L): | 6.25

## nh3fres2
Freshwater un-ionized ammonia criteria based on EPA Gold Book
(EPA 440/5-86-001) as revised by Heber and Ballentine (1992).
Based on Lotus File NH3FRES2.WK1 Revised 12-Dec-94
INPUT
1. Temperature (deg C; 0<T<30): | 20
2. pH (6.5<pH<9.0): | 7.25
3. Total Ammonia (ug N/L): | 200
4. Acute TCAP (Salmonids present- 20; absent- 25): | 20
5. Chronic TCAP (Salmonids present- 15; absent- 20): | 15
OUTPUT
1. Intermediate Calculations:
Acute FT: | 1
Chronic FT: | 1.4125
FPH: | 1.93
RATIO: | 23.6565
pKa: | 9.401
Fraction Of Total Ammonia Present As Un-ionized: | 0.7014%
2. Sample Un-ionized Ammonia Concentration (ug/L as NH3-N): | 1.4029
3. Un-ionized Ammonia Criteria:
Acute (1-hour) Un-ionized Ammonia Criterion (ug/L as NH3-N): | 110.734
Chronic (4-day) Un-ionized Ammonia Criterion (ug/L as NH3-N): | 10.1964
4. Total Ammonia Criteria:
Acute Total Ammonia Criterion (ug/L as NH3-N): | 15786.8593
Chronic Total Ammonia Criterion (ug/L as NH3-N): | 1453.6553

## nh3fresh
Freshwater un-ionized ammonia criteria based on EPA Gold Book
(EPA 440/5-86-001).
Based on Lotus File NH3FRESH.WK1 Revised 19-Oct-93
INPUT
1. Temperature (deg C; 0<T<30): | 20
2. pH (6.5<pH<9.0): | 9
3. Total Ammonia (ug N/L): | 200
4. Acute TCAP (Salmonids present- 20; absent- 25): | 20
5. Chronic TCAP (Salmonids present- 15; absent- 20): | 15
OUTPUT
1. Intermediate Calculations:
Acute FT: | 1
Chronic FT: | 1.4125
FPH: | 1
RATIO: | 16
pKa: | 9.401
Fraction Of Total Ammonia Present As Un-ionized: | 28.43%
2. Sample Un-ionized Ammonia Concentration (ug/L as NH3-N): | 56.8597
3. Un-ionized Ammonia Criteria:
Acute (1-hour) Un-ionized Ammonia Criterion (ug/L as NH3-N): | 213.72
Chronic (4-day) Un-ionized Ammonia Criterion (ug/L as NH3-N): | 29.0966
4. Total Ammonia Criteria:
Acute Total Ammonia Criterion (ug/L as NH3-N): | 751.7454
Chronic Total Ammonia Criterion (ug/L as NH3-N): | 102.3452

## nh3salt
Calculation of seawater fraction of un-ionized ammonia
from Hampson (1977). Un-ionized ammonia criteria for
salt water are from EPA 440/5-88-004.
Based on Lotus File NH3SALT.WK1 Revised 19-Oct-93
INPUT
1. Temperature (deg C): | 15
2. pH: | 8
3. Salinity (g/Kg): | 20
OUTPUT
1. Pressure (atm; EPA criteria assumes 1 atm): | 1
2. Molal Ionic Strength (not valid if >0.85): | 0.40672
3. pKa8 at 25 deg C (Whitfield model "B"): | 9.2922
4. Percent of Total Ammonia Present as Unionized: | 2.362%
5. Unionized ammonia criteria (mg un-ionized NH3 per liter)
from EPA 440/5-88-004
Acute: | 0.233
Chronic: | 0.035
6. Total Ammonia Criteria (mg/L as NH3)
Acute: | 9.8642
Chronic: | 1.4817
7. Total Ammonia Criteria (mg/L as NH3-N)
Acute: | 8.1084
Chronic: | 1.218

## phmix2
Calculation of pH of a mixture of two flows. Based on the
procedure in EPA's DESCON program (EPA, 1988. Technical
Guidance on Supplementary Stream Design Conditions for Steady
State Modeling. USEPA Office of Water, Washington D.C.)
Based on Lotus File PHMIX2.WK1 Revised 19-Oct-93
INPUT
1. DILUTION FACTOR AT MIXING ZONE BOUNDARY | 2
1. UPSTREAM/BACKGROUND CHARACTERISTICS
Temperature (deg C): | 12
pH: | 7.5
Alkalinity (mg CaCO3/L): | 50
2. EFFLUENT CHARACTERISTICS
Temperature (deg C): | 20
pH: | 7.2
Alkalinity (mg CaCO3/L): | 150
OUTPUT
1. IONIZATION CONSTANTS
Upstream/Background pKa: | 6.4457
Effluent pKa: | 6.382
2. IONIZATION FRACTIONS
Upstream/Background Ionization Fraction: | 0.91891
Effluent Ionization Fraction: | 0.86801
3. TOTAL INORGANIC CARBON
Upstream/Background Total Inorganic Carbon (mg CaCO3/L): | 54.4121
Effluent Total Inorganic Carbon (mg CaCO3/L): | 172.8082
4. CONDITIONS AT MIXING ZONE BOUNDARY
Temperature (deg C): | 16
Alkalinity (mg CaCO3/L): | 100
Total Inorganic Carbon (mg CaCO3/L): | 113.6102
pKa: | 6.4119
pH at Mixing Zone Boundary: | 7.2781

## rivplum5
Spread of a plume from a point source in a river with boundary effects from the shoreline
based on the method of Fischer et al. (1979) with correction for the effective origin of effluent.
Revised 22-Feb-96
INPUT
1. Effluent Discharge Rate (cfs): | 5.5699
2. Receiving Water Characteristics Downstream From Waste Input
Stream Depth (ft): | 0.89555
Stream Velocity (fps): | 1.7164
Channel Width (ft): | 114.221
Stream Slope (ft/ft) or Manning roughness "n": | 0.007
0 if slope or 1 if Manning "n" in previous cell: | 0
3. Discharge Distance From Nearest Shoreline (ft): | 0
4. Location of Point of Interest to Estimate Dilution
Distance Downstream to Point of Interest (ft): | 300
Distance From Nearest Shoreline (ft): | 0
5. Transverse Mixing Coefficient Constant (usually 0.6): | 0.6
6. Original Fischer Method (enter 0) or Effective Origin Modification (enter 1) | 0
OUTPUT
1. Source Conservative Mass Input Rate
Concentration of Conservative Substance (%): | 100
Source Conservative Mass Input Rate (cfs*%): | 556.992
2. Shear Velocity
Shear Velocity based on slope (ft/sec): | 0.44928
Shear Velocity based on Manning "n":
using Prasuhn equations 8-26 and 8-54 assuming
hydraulic radius equals depth for wide channel
Darcy-Weisbach friction factor "f": | #N/A
Shear Velocity from Darcy-Weisbach "f" (ft/sec): | #N/A
Selected Shear Velocity for next step (ft/sec): | 0.44928
3. Transverse Mixing Coefficient (ft2/sec): | 0.24141
4. Plume Characteristics Accounting for Shoreline Effect (Fischer et al., 1979)
Co | 3.1725
x' | 0.0032343
y'o | 0
y' at point of interest | 0
Solution using superposition equation (Fischer eqn 5.9)
Term for n= -2 | 0
Term for n= -1 | 1.0512e-134
Term for n= 0 | 2
Term for n= 1 | 1.0512e-134
Term for n= 2 | 0
Upstream Distance from Outfall to Effective Origin of Effluent Source (ft) | #N/A
Effective Distance Downstream from Effluent to Point of Interest (ft) | 300
x' Adjusted for Effective Origin | 0.0032343
C/Co (dimensionless) | 9.9206
Concentration at Point of Interest (Fischer Eqn 5.9) | 31.4729
Unbounded Plume Width at Point of Interest (ft) | 36.7459
Unbounded Plume half-width (ft) | 18.3729
Distance from near shore to discharge point (ft) | 0
Distance from far shore to discharge point (ft) | 114.221
Plume width bounded by shoreline (ft) | 18.3729
Approximate Downstream Distance to Complete Mix (ft): | 37102.7517
Theoretical Dilution Factor at Complete Mix: | 31.5211
Calculated Flux-Average Dilution Factor Across Entire Plume Width: | 5.0703
Calculated Dilution Factor at Point of Interest: | 3.1773

## wqbp2
Water Quality-Based Permit Limits for acute and chronic criteria.
(based on EPA/505/2-90-001 Box 5-2).
Based on Lotus File WQBP2.WK1 Revised 19-Oct-93
INPUT
1. Water Quality Standards (Concentration)
Acute (one-hour) Criteria: | 19
Chronic (n-day) Criteria: | 11
2. Upstream Receiving Water Concentration
Upstream Concentration for Acute Condition (7Q10): | 0
Upstream Concentration for Chronic Condition (7Q10): | 0
3. Dilution Factors (1/{Effluent Volume Fraction})
Acute Receiving Water Dilution Factor at 7Q10: | 26
Chronic Receiving Water Dilution Factor at 7Q10: | 100
4. Coefficient of Variation for Effluent Concentration
(use 0.6 if data are not available): | 0.6
5. Number of days (n1) for chronic average
(usually four or seven; four is recommended): | 4
6. Number of samples (n2) required per month for monitoring: | 30
OUTPUT
1. Z Statistics
LTA Derivation (99%tile): | 2.326
Daily Maximum Permit Limit (99%tile): | 2.326
Monthly Average Permit Limit (95%tile): | 1.645
2. Calculated Waste Load Allocations (WLA's)
Acute (one-hour) WLA: | 494
Chronic (n1-day) WLA: | 1100
3. Derivation of LTAs using April 1990 TSD (Box 5-2 Step 2 & 3)
Sigma^2: | 0.30748
Sigma^2-n1: | 0.086178
LTA for Acute (1-hour) WLA: | 158.6151
LTA for Chronic (n1-day) WLA: | 580.1768
Most Limiting LTA (minimum of acute and chronic): | 158.6151
4. Derivation of Permit Limits From Limiting LTA (Box 5-2 Step 4)
Sigma^2-n2: | 0.011929
Daily Maximum Permit Limit: | 494
Monthly Average Permit Limit: | 188.704